## Sheet1
ALC Controller
|  |  | Hardware | Hardware/Webctrl Settings
Board-Slot | Channel |  | Name | Display name |  | I/O Type | Sensor/Actuator Type | Min/Max | Exp:Num
DS6241 D/A - 16 | 3 | VAV-1 | ZN431A | Space Temp | AI | 0-5V | Linear Full Range | 25/125F | 00:01 | This AI input is from VAV-6 IN1
| 1 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01
| 5 |  |  | Flow Input | AI | 0-10V | Linear Full Range | 0/1400 | 00:02
| 4 | VAV-2 | ZN431A | Space Temp | AI | 0-5V | Linear Full Range | 25/125F | 00:01 | This AI input is from VAV-7 IN1
| 2 |  |  | Supply air temperature | AI | 0-5V | Linear Full Range | 45/95F | 00:01
| 6 |  |  | Flow Input | AI | 0-10V | Linear Full Range | 0/1400 | 00:02
| 8 | OA | OF 1628-NR | OA Temp | AI | 0-10 V | Linear Full Range | -20/120F | 00:01
| 7 |  |  | OA Humidity | AI | 0-10 V | Linear Full Range | 0/100 | 00:02
| 9 | VAV-3 | ZN431A | Space Temp | AI | 0-5V |  |  |  | This AI input is from VAV-8 IN1
| 10 |  |  | Supply air temperature | AI | 0-5V
| 11 |  |  | Flow Input | AI | 0-10V
| 12 | VAV-4 | ZN431A | Space Temp | AI | 0-5V |  |  |  | This AI input is from VAV-9 IN1
| 13 |  |  | Supply air temperature | AI | 0-5V
| 14 |  |  | Flow Input | AI | 0-10V
| 15 | VAV-5 | ZN431A | Space Temp | AI | 0-5V |  |  |  | This AI input is from VAV-10 IN1
| 16 |  |  | Supply air temperature | AI | 0-5V
| 17 |  |  | Flow Input | AI | 0-10V